## Introduction
www.rletech.com 800.518.1519
Thank you for your interest in the Falcon FMS. Deisgned and engineered to be robust, reliable, and scalable, there is an FMS well-suited for every facility.
The workbook contains several tabs: • Introduction - Outlines how to use this file. • Specifications - Details FMS specifications. • Example - An example of how to complete the worksheet. • Worksheet - Our Falcon Selection Worksheet will help you understand the facility's requirements so you can spec the right FMS for the job.
Additional information including the Data Sheet, User Guide and product videos for the FMS is available on our web site - http://rletech.com/fms/
We hope this overview helps you gain a more thorough understanding of the FMS, its capabilities, and its application in your facility. If you have additional questions, feel free to contact us at 800.518.1519. We're available Monday through Friday, 8:00 a.m. through 5:00 p.m. MST.

## Specifications
www.rletech.com 800.518.1519
Before you begin to design a FMS system, take a few minutes to understand the FMS's capabilities and the different FMS configurations.
Inputs | Each FMS accepts a specific number of wired inputs. Depending on the selected configuration , the FMS accepts the following types of signals: • Dry contacts • 4-20Ma • 0-5VDC • 0-10VDC Alarm thresholds can be set and when conditions for an input exceed acceptable limits, direct alarm notification will occur.
Communications | The Falcon FMS can also easily be integrated into an existing management system. It can accept the following protocols: • SNMP • Modbus • BACnet
Power | The FMS can accommodate either 24VDC (power supply w/ U.S. blade included) or 48VDC (hardwired directly into the FMS). You will need to designate how the unit will be powered when you order the FMS, so you receive the right unit for your application.
Configurations | The FMS base unit is available in a 1 rack unit (RU) and 2RU height configuration. Expansion cards can be added to the FMS to accommodate additional inputs and relay outputs beyond the base functionality. • The 1RU can accommodate a single additional expansion card. • The 2RU can accommodate up to four expansion cards. When you're deciding which height FMS to purchase, be sure to consider future expansion possibilities. Many customers purchase a 2RU FMS so they have room to add multiple expansion cards in the future.
Base Units | Base FMS models accommodate 8 universal inputs (dry contacts and/or 4-20mA inputs) and have 2 relay outputs. • Each "x" in the base unit product code designates an empty expansion card slot that can be populated with one of two different expansion cards (EXP-A and EXP-C). • An internal temperature/humidity sensor can also be ordered as part of an FMS base unit. The "Y" or "n" in the base unit product code designates whether the unit has an internal temperature/humidity sensor or not. The following FMS base units are available:
|  | FMS BASE UNIT DESCRIPTION | PRODUCT CODE
|  | 1 RU, 1 available expansion card slot, includes (US) 100-240VAC to 24VDC wall adapter | FMS-x-n-24
|  | 1 RU, 1 available expansion card slot, internal temp/humidity sensor, includes (US) 100-240VAC to 24VDC wall adapter | FMS-x-Y-24
|  | 1 RU, 1 available expansion card slot, requires 48VDC | FMS-x-n-48
|  | 1 RU, 1 available expansion card slot, internal temp/humidity sensor, requires 48VDC | FMS-x-Y-48
|  | 2 RU, 4 available expansion card slots, includes 85-264VAC desktop adapter with (US) cord | FMS-xxxx-n-24
|  | 2 RU, 4 available expansion card slots, internal temp/humidity sensor, includes 85-264VAC desktop adapter with (US) cord | FMS-xxxx-Y-24
|  | 2 RU, 4 available expansion card slots, requires 48VDC | FMS-xxxx-n-48
|  | 2 RU, 4 available expansion card slots, internal temp/humidity sensor, requires 48VDC | FMS-xxxx-Y-48
Expansion Cards | Expansion cards can be added to the FMS to accommodate additional inputs beyond the base 8 inputs and additional relay outputs beyond the base 2 relay outputs.
|  | FMS EXPANSION CARD DESCRIPTION | PRODUCT CODE
|  | A Card: 12 universal inputs (N/O Dry Contact, 4-20mA, 0-5 VDC, 0-10 VDC) and 8 relay outputs. For use with 24VDC or 48VDC models. Limit one A card per 48VDC FMS. | EXP-A-24/48
|  | C Card (24VDC): 24 digital inputs. For use with 24VDC models only. | EXP-C-24
|  | C Card (48VDC): 12 digital inputs. For use with 48VDC models. | EXP-C-48
Optional Modem | An internal PPP enabled modem can be added allow access to the Falcon and direct alarm notification through phone lines even if network connectivity is lost. The internal modem (EXP-IM) does not utilize an expansion card slot.
Mounting | The FMS is shipped with rack mount brackets that allow it to be mounted in a computer rack. Wall mount brackets are available for an additional charge.

## Example
Falcon Selection Worksheet
|  | Customer / Job #: |  |  |  |  | Contact:
Include the total quantities of each device and signal type from each device listed.
Digital Inputs: NO/NC (Form C) output relays available from sensors or equipment.
4-20mA: Analog signal from sensor
0-5VDC / 0-10VDC: Analog signal from sensor
Modbus Registers: Registers available from integrated equipment
SNMP: OIDs available for integration
BACnet Instances: RInstances available from integrated equipment
Relay Outputs: NO/NC Dry Contact relay output from the Falcon product to another device.
IP Links: External IP addressable devices that may be linked to from the Falcon.
NOTE: A single combination temperature and humidity sensor will have two output signals
|  |  |  | Digital |  | 0-5VDC | Modbus | SNMP | BACnet | Relay
| Device Description |  | QTY | Inputs | 4-20mA | 0-10VDC | Registers | OIDs | Instances | Outputs | IP Links
1 | Wired temperature sensors |  | 15 |  | 15
2 | Wired temp/hum sensors |  | 5 |  | 10
3 | Magnetic door sensors |  | 8 | 8
4 | Motion sensors |  | 4 | 4
5 | Smoke detectors |  | 2 | 2
6 | UPS 1 summary alarms |  | 5 | 5
7 | UPS 2 summary alarms |  | 5 | 5
8 | A/C 1 |  | 1 |  |  |  |  | 13
9 | A/C 2 |  | 1 |  |  |  |  | 13
10 | A/C 3 |  | 1 |  |  |  |  | 13
11 | A/C 4 |  | 1 |  |  |  |  | 13
12 | PDU 1 |  | 1 |  |  |  | 56
13 | PDU 2 |  | 1 |  |  |  | 56
14 | IP cameras |  | 6 | [7 empty] | 6
15 | Wireless gateway |  | 1 |  |  |  | 100
16 | Distance-read leak detection |  | 1 |  |  |  |  | 5 |  |  | 1
17 | Spot detectors |  | 4 | 4
18 | Generator |  | 1 |  |  |  | 20 |  |  |  | 1
19 | Wireless temperature sensors |  | 45
20 | Wireless temp/hum sensors |  | 10
21 | FMS output to IP camera | [8 empty] | 6
22 | FMS output to valve | [8 empty] | 1
23 | FMS output to Generator | [8 empty] | 1
24
25
26
27
28
|  |  | Totals: | 28 | 25 | 0 | 232 | 57 | 0 | 8 | 8
|  |  |  | Digital | 4-20mA | 0-5 VDC | Modbus | SNMP | BACnet | Relay | IP Links
|  |  |  | Inputs |  | 0-10 VDC | Registers | OIDs | Instances | Outputs
|  | Available power: |  | 110/220 VAC: |  | x |  | 48VDC:
[8 empty] | Total SECONDARY devices communicating SNMP, Modbus or BACnet: | 9
|  |  |  | Internal Modem required: | Yes: | X | No:
[5 empty] | Recommended Falcon Product: | FMS-AACx-n-24

## Worksheet
Falcon Selection Worksheet
|  | Customer / Job #: |  |  |  |  | Contact:
Include the total quantities of each device and signal type from each device listed.
Digital Inputs: NO/NC (Form C) output relays available from sensors or equipment.
4-20mA: Analog signal from sensor
0-5VDC / 0-10VDC: Analog signal from sensor
Modbus Registers: Registers available from integrated equipment
SNMP: OIDs available for integration
BACnet Instances: RInstances available from integrated equipment
Relay Outputs: NO/NC Dry Contact relay output from the Falcon product to another device.
IP Links: External IP addressable devices that may be linked to from the Falcon.
NOTE: A single combination temperature and humidity sensor will have two output signals
|  |  |  | Digital |  | 0-5VDC | Modbus | SNMP | BACnet | Relay
| Device Description |  | QTY | Inputs | 4-20mA | 0-10VDC | Registers | OIDs | Instances | Outputs | IP Links
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
|  |  | Totals: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Digital | 4-20mA | 0-5 VDC | Modbus | SNMP | BACnet | Relay | IP Links
|  |  |  | Inputs |  | 0-10 VDC | Registers | OIDs | Instances | Outputs
|  | Available power: |  | 110/220 VAC: |  |  |  | 48VDC:
Total SECONDARY devices communicating SNMP, Modbus or BACnet:
|  |  |  | Internal Modem required: | Yes: |  | No:
Recommended Falcon Product: